Copyright 2019 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

This Product MasterSpec Section is licensed by Deltek, Inc. to HoldRite, Division of RWC Corporation ("Licensee").

This Product MasterSpec Section modifies the original MasterSpec text and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, Deltek or The American Institute of Architects (AIA). Neither AIA nor Deltek are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user. A qualified design professional should review and edit the document to suit project requirements.

For more information, contact HoldRite, Division of RWC Corporation, 14284 Danielson St., Poway, CA 92064 Phone: (800) 321-0316 | (760) 744-6944; Fax: (760) 744-0507; Website: holdrite.com; Email: Jeff.hamilton@rwc.com.

For information about MasterSpec, contact Deltek at (800) 424-5080 or visit masterspec.com.

SECTION 078413 - PENETRATION FIRESTOPPING

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Access Product MasterSpec Sections:

<Double click here to view the list of manufacturer Sections available at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

Penetration firestopping systems for the following applications:

Penetrations in fire-resistance-rated walls.

Penetrations in horizontal assemblies.

Penetrations in smoke barriers.

Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Section 078443 "Joint Firestopping" for joints in or between fire-resistance-rated construction, at exterior curtain-wall/floor intersections, and in smoke barriers.

Section 220517 "Sleeves and Sleeve Seals for Plumbing Piping."

ALLOWANCES

Retain products and Work included in this Section that are covered by cash or quantity allowance. Do not include amounts. Insert descriptions of items in Part 2 or 3 to provide information affecting the cost of the Work that is not included under the allowance.

Penetration firestopping Work is part of an allowance.

UNIT PRICES

Retain this article if Work specified in this Section is measured and paid for under the provisions of unit prices. Do not include amounts. Insert descriptions of items in Part 2 or 3 to provide information affecting the cost of the Work that is not included under the unit price.

Work of this Section is affected by unit prices.

PREINSTALLATION MEETINGS

Retain "Preinstallation Conference" Paragraph below if Work of this Section is extensive or complex enough to justify a conference.

Preinstallation Conference: Conduct conference at [Project site] <Insert location> two weeks prior to firestopping and associated work.

If needed, revise subparagraphs below to include conference participants not mentioned in Section 013100 "Project Management and Coordination."

Authorities Having Jurisdiction.

Contractor.

Construction Manager.

Firestopping Manufacturer's Representative.

Firestopping Subcontractor.

Installer of associated work, including architectural, mechanical, electrical and communication work.

Testing agencies.

Owner.

Owner's Insurers.

<Insert participants>.

ACTION SUBMITTALS

Product Data: For each type of firestop material to be installed.

Product characteristics and limitation criteria.

Preparation requirements and application instructions.

Material safety data sheets (MSDS) or safety data sheets (SDS).

Sustainable Design Submittals:

"Product Data" Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. Coordinate with requirements for sealants.

Product Data: For sealants, indicating VOC content.

"Laboratory Test Reports" Subparagraph below applies to LEED 2009 for Schools, LEED v4, IgCC, ASHRAE 189.1, and Green Globes. Coordinate with requirements for sealants.

Laboratory Test Reports: For sealants, indicating compliance with requirements for low-emitting materials.

Product Schedule: For each penetration firestopping system. Include location, illustration of firestopping system, and design designation of qualified testing and inspecting agency.

Retain "Engineering Judgments" Subparagraph below only after verifying that authorities having jurisdiction will accept modifications handled by method in subparagraph.

Engineering Judgments: Where Project conditions require modification to a qualified testing and inspecting agency's illustration for a particular penetration firestopping system, submit illustration, with modifications marked, approved by penetration firestopping system manufacturer's fire-protection engineer as an engineering judgment or equivalent fire-resistance-rated assembly. Obtain approval of authorities having jurisdiction prior to submittal.

INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

Qualification Data: For Installer.

Product Test Reports: For each penetration firestopping system, for tests performed by a qualified testing agency.

CLOSEOUT SUBMITTALS

Installer Certificates: From Installer indicating that penetration firestopping systems have been installed in compliance with requirements and manufacturer's written instructions.

QUALITY ASSURANCE

Installer Qualifications: A firm experienced in installation of penetration firestopping similar in material, design, and extent to that indicated for this Project and whose work has resulted in construction with a record of successful in-service performance.

Manufacturer's willingness to sell its products to Contractor or Installer engaged by Contractor does not confer qualifications on buyer.

Provide written evidence of qualifications and experience. Qualifications include having the necessary experience, staff, and training to install manufacturer's products in accordance with requirements.

PROJECT CONDITIONS

Environmental Limitations: Do not install penetration firestopping system when ambient or substrate temperatures are outside limits permitted by penetration firestopping system manufacturers or when substrates are wet because of rain, frost, condensation, or other causes.

Install and cure penetration firestopping materials in accordance with manufacturer's written instructions using natural means of ventilations or, where this is inadequate, forced-air circulation.

COORDINATION

Coordinate construction of openings and penetrating items to ensure that penetration firestopping systems can be installed in accordance with specified firestopping system design.

Coordinate sizing of sleeves, openings, core-drilled holes, or cut openings to accommodate penetration firestopping systems.

WARRANTY

When warranties are required, verify with Owner's counsel that warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

Retain "Special Warranty" Paragraph below when roof specialties are required to be included in a roofing-membrane manufacturer's system warranty; coordinate with Project roofing-membrane Section.

Special Warranty: Manufacturer and Installer agree to repair or replace firestop system that does not perform as tested within the specified warranty period.

Verify available warranties and warranty periods.

Warranty Period: Two years from date of Substantial Completion.

PRODUCTS

Manufacturers and products listed in SpecAgent and MasterWorks Paragraph Builder are neither recommended nor endorsed by the AIA or Deltek. Before inserting names, verify that manufacturers and products listed there comply with requirements retained or revised in descriptions and are both available and suitable for the intended applications. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

PERFORMANCE REQUIREMENTS

Fire-Test-Response Characteristics:

Penetration firestopping system tests to be performed by a qualified testing agency acceptable to authorities having jurisdiction.

Test in accordance with testing standards referenced in "Penetration Firestopping Systems" Article. Provide rated systems complying with the following requirements:

Penetration firestopping systems shall bear classification marking of a qualified testing agency.

Retain only subparagraphs below that reference the directories of testing and inspecting agency or agencies approved by authorities having jurisdiction.

UL in its "Fire Resistance Directory."

Intertek Group in its "Directory of Listed Building Products."

FM Approval in its "Approval Guide."

<Insert name of qualified testing and inspecting agency>.

VOC Content: Products shall comply with VOC content [limits of authorities having jurisdiction] [when calculated in accordance with 40 CFR 59, Subpart D (EPA Method 240)] unless otherwise indicated.

Retain subparagraph below for VOC content if retaining second option in "VOC Content" Paragraph above.

Sealants: 250 g/L.

Sealant Primers for Nonporous Substrates: 250 g/L.

Sealant Primer for Porous Substrates: 775 g/L.

PENETRATION FIRESTOPPING SYSTEMS

Penetration Firestopping Systems: Systems that resist spread of fire and passage of smoke and other gases, and that maintain original fire-resistance rating of construction penetrated. Penetration firestopping systems shall be compatible with one another, with the substrates forming openings, and with penetrating items if any.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

For HoldRite's "HydroFlame Corrugated Metal Deck Firestop Systems," see holdrite.com/corrugated-metal-deck; for "HydroFlame Flat Form Deck Firestop Systems," see holdrite.com/firestop-flat-form-deck.

Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of RWC Corporation; HydroFlame [Corrugated Metal] [Flat Form] Deck Firestop Systems or comparable product by one of the following:

3M Fire Protection Products.

A/D Fire Protection Systems Inc.

Passive Fire Protection Partners.

<Insert manufacturer's name>.

Penetrations in Fire-Resistance-Rated Walls: Penetration firestopping systems with ratings determined in accordance with ASTM E814 or UL 1479, based on testing at a positive pressure differential of 0.01 inch wg (2.49 Pa).

Rating in "F-Rating" Subparagraph below indicates resistance to flame spread.

F-Rating: Not less than the fire-resistance rating of constructions penetrated.

Penetrations in Horizontal Assemblies: Penetration firestopping systems with ratings determined in accordance with ASTM E814 or UL 1479, based on testing at a positive pressure differential of 0.01 inch wg (2.49 Pa).

Ratings in "F-Rating" Subparagraph below indicate resistance to flame spread.

F-Rating: At least one hour, but not less than the fire-resistance rating of constructions penetrated.

Ratings in "T-Rating" Subparagraph below indicate resistance to excessive thermal transmission.

T-Rating: At least one hour, but not less than the fire-resistance rating of constructions penetrated, except for floor penetrations within the cavity of a wall.

Ratings in "W-Rating" Subparagraph below indicate resistance to water leakage. W-ratings are not required by the IBC but may be needed if water leakage is a concern.

W-Rating: Provide penetration firestopping systems showing no evidence of water leakage when tested in accordance with UL 1479.

Retain "Penetrations in Smoke Barriers" Paragraph below if smoke barriers are included in Project, and indicate locations on Drawings. Coordinate with the Penetration Firestopping System Schedule.

Penetrations in Smoke Barriers: Penetration firestopping systems with ratings determined in accordance with UL 1479, based on testing at a positive pressure differential of 0.30 inch wg (74.7 Pa).

Ratings in "L-Rating" Subparagraph below indicate resistance to air leakage.

L-Rating: Not exceeding 5.0 cfm/sq. ft. (0.025 cu. m/s per sq. m) of penetration opening at and no more than 50 cfm (0.024 cu. m/s) cumulative total for any 100 sq. ft. (9.3 sq. m) at both ambient and elevated temperatures.

Exposed Penetration Firestopping Systems: Flame-spread and smoke-developed indexes of less than 25 and 450, respectively, in accordance with ASTM E84.

First subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes.

Sealant shall have a VOC content of 250 g/L or less.

First subparagraph below applies to LEED 2009 for Schools, IEQc 4.1.

Sealant shall comply with testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

First subparagraph below applies to LEED v4.

Sealant shall comply with testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

First subparagraph below applies to IgCC.

Sealant shall comply with testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers." Formaldehyde emissions shall not exceed 9 mcg/cu. m or 7 ppb, whichever is less.

First subparagraph below applies to ASHRAE 189.1.

Sealant shall comply with testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Subparagraph below applies to Green Globes.

Sealant shall comply with testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers." The building concentration of formaldehyde shall not exceed half of the indoor recommended exposure limit, or 33 mcg/cu. m, and that of acetaldehyde shall not exceed 9 mcg/cu. m.

System in "Manufactured Piping Penetration Firestopping System" Paragraph below is installed when the piping is installed. Verify availability of F-ratings, T-ratings, and W-ratings. When this Section was updated, ProVent Systems was the only manufacturer to offer this type of firestopping system.

Manufactured Piping Penetration Firestopping System: Penetration firestopping systems with ratings determined in accordance with ASTM E814 or UL 1479, based on testing at a positive pressure differential of 0.01 inch wg (2.49 Pa).

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of RWC Corporation; HydroFlame Firestop Systems or comparable product by one of the following:

ProVent Systems, Inc.

<Insert manufacturer's name>.

Rating in "F-Rating" Subparagraph below indicates resistance to flame spread.

F-Rating: At least one hour, but not less than the fire-resistance rating of constructions penetrated.

Ratings in "T-Rating" Subparagraph below indicate resistance to excessive thermal transmission.

T-Rating: At least one hour, but not less than the fire-resistance rating of constructions penetrated except for floor penetrations within the cavity of a wall.

Ratings in "W-Rating" Subparagraph below indicate resistance to water leakage. W-ratings are not required by the IBC but may be needed if water leakage is a concern.

W-Rating: Provide penetration firestopping systems showing no evidence of water leakage when tested in accordance with UL 1479.

Sleeve: Molded-PVC plastic, of length to match slab thickness and with integral nailing flange on one end for installation in cast-in-place concrete slabs.

Fitting in "Stack Fitting" Subparagraph below is for use with plastic stacks.

Stack Fitting: ASTM A48/A48M, gray-iron, hubless-pattern wye branch with neoprene O-ring at base and gray-iron plug in thermal-release harness. Include PVC protective cap for plug.

Coating in "Special Coating" Subparagraph below is for use with corrosion-resistant plastic stacks.

Special Coating: Corrosion resistant on interior of fittings.

Accessories: Provide components for each penetration firestopping system that are needed to install fill materials and to maintain ratings required. Use only those components specified by penetration firestopping system manufacturer and approved by qualified testing and inspecting agency for conditions indicated.

Retain accessories in subparagraphs below as required.

Permanent forming/damming/backing materials.

Substrate primers.

Collars.

Steel sleeves.

FILL MATERIALS

If fill materials are Contractor's choice, retain only those paragraphs below that suit Project. If retaining fill materials in the Penetration Firestopping System Schedule, coordinate paragraphs with materials specified in schedule.

HoldRite devices are UL W-rated with no additional accessories required.

Cast-in-Place Firestop Devices: Factory-assembled devices for use in cast-in-place concrete floors and consisting of an outer sleeve lined with an intumescent strip, a flange attached to one end of the sleeve for fastening to concrete formwork, and a neoprene gasket.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of RWC Corporation; HydroFlame Sleeves.

System Accessories: Provide components for a complete UL-rated system.

Aerator Adaptor: Provide with aerator systems.

Tub Box Kit: Provide with tub installations.

Closet Flange Sleeve: Provide with toilet flanges.

Water Dam.

Floor Drain Sleeves.

Shower Drain Sleeves.

Water Modules.

Latex Sealants: Single-component latex formulations that do not re-emulsify after cure during exposure to moisture.

Retain "Basis-of-Design Product" Subparagraph below to identify a specific product.

Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of RWC Corporation; HydroFlame [100 General Purpose Firestop] [200 High Performance Intumescent] Sealant.

Firestop Devices: Factory-assembled collars formed from galvanized steel and lined with intumescent material sized to fit specific diameter of penetrant.

Retain "Basis-of-Design Product" Subparagraph below to identify a specific product.

Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of RWC Corporation; HydroFlame [Drop In Device] [Pipe Collar].

Intumescent Composite Sheets: Rigid panels consisting of aluminum-foil-faced intumescent elastomeric sheet bonded to galvanized-steel sheet.

Intumescent Putties: Nonhardening, water-resistant, latex-based, intumescent putties containing no solvents or inorganic fibers.

Retain "Basis-of-Design Product" Subparagraph below to identify a specific product.

Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of RWC Corporation; HydroFlame Putty Pad.

Intumescent Wrap Strips: Single-component, latex-based intumescent elastomeric sheets that form a char when activated by heat, causing the material to expand forming an insulation layer.

Retain "Basis-of-Design Product" Subparagraph below to identify a specific product.

Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of RWC Corporation; HydroFlame Wrap Strips.

Mortars: Prepackaged dry mixes consisting of a blend of inorganic binders, hydraulic cement, fillers and lightweight aggregate formulated for mixing with water at Project site to form a nonshrinking, homogeneous mortar.

Pillows/Bags: Reusable heat-expanding pillows/bags consisting of glass-fiber cloth cases filled with a combination of mineral-fiber, water-insoluble expansion agents, and fire-retardant additives. Where exposed, cover openings with steel-reinforcing wire mesh to protect pillows/bags from being easily removed.

Silicone Foams: Multicomponent, silicone-based liquid elastomers that, when mixed, expand and cure in place to produce a flexible, nonshrinking foam.

Silicone Sealants: Single-component, silicone-based, neutral-curing elastomeric sealants.

Retain "Basis-of-Design Product" Subparagraph below to identify a specific product.

Retain one of two options below. HoldRite's "HydroFlame 300 CG" is caulk grade, and its "HydroFlame 300 SL" is self-leveling.

Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of RWC Corporation; [HydroFlame 300 CG] [HydroFlame 300 SL].

MIXING

Retain this article if products are specified that require mixing before application.

Penetration Firestopping Materials: For those products requiring mixing before application, comply with penetration firestopping system manufacturer's written instructions for accurate proportioning of materials, water (if required), type of mixing equipment, selection of mixer speeds, mixing containers, mixing time, and other items or procedures needed to produce products of uniform quality with optimum performance characteristics for application indicated.

EXECUTION

EXAMINATION

Examine substrates and conditions, with Installer present, for compliance with requirements for opening configurations, penetrating items, substrates, and other conditions affecting performance of the Work.

Proceed with installation only after unsatisfactory conditions have been corrected.

PREPARATION

Surface Cleaning: Before installing penetration firestopping systems, clean out openings immediately to comply with manufacturer's written instructions and with the following requirements:

Remove from surfaces of opening substrates and from penetrating items foreign materials that could interfere with adhesion of penetration firestopping materials.

Clean opening substrates and penetrating items to produce clean, sound surfaces capable of developing optimum bond with penetration firestopping materials. Remove loose particles remaining from cleaning operation.

Remove laitance and form-release agents from concrete.

Retain paragraph below if products selected require priming.

Prime substrates where recommended in writing by manufacturer, using that manufacturer's recommended products and methods. Confine primers to areas of bond; do not allow spillage and migration onto exposed surfaces.

INSTALLATION

General: Install penetration firestopping systems to comply with manufacturer's written installation instructions and published drawings for products and applications.

Install forming materials and other accessories of types required to support fill materials during their application and in the position needed to produce cross-sectional shapes and depths required to achieve fire ratings.

After installing fill materials and allowing them to fully cure, remove combustible forming materials and other accessories not forming permanent components of firestopping.

Install fill materials by proven techniques to produce the following results:

Fill voids and cavities formed by openings, forming materials, accessories, and penetrating items to achieve required fire-resistance ratings.

Apply materials so they contact and adhere to substrates formed by openings and penetrating items.

For fill materials that will remain exposed after completing the Work, finish to produce smooth, uniform surfaces that are flush with adjoining finishes.

IDENTIFICATION

Wall Identification: Permanently label walls containing penetration firestopping systems with the words "Fire and/or Smoke Barrier - Protect All Openings," using lettering not less than 3 inches (76 mm) high and with minimum 0.375-inch (9.5-mm) strokes.

Locate in accessible concealed floor, floor-ceiling, or attic space at 15 ft. (4.57 m) from end of wall and at intervals not exceeding 30 ft. (9.14 m).

Retain "Penetration Identification" Paragraph below if required. Individual joint penetration labeling may not be required by authorities having jurisdiction if wall is identified, but labeling is useful if penetration firestopping systems must be replaced.

Penetration Identification: Identify each penetration firestopping system with legible metal, or plastic labels. Attach labels permanently to surfaces adjacent to and within 6 inches (150 mm) of penetration firestopping system edge so labels are visible to anyone seeking to remove penetrating items or firestopping systems. Use mechanical fasteners or self-adhering-type labels with adhesives capable of permanently bonding labels to surfaces on which labels are placed. Include the following information on labels:

The words "Warning - Penetration Firestopping - Do Not Disturb. Notify Building Management of Any Damage."

Contractor's name, address, and phone number.

Designation of applicable testing and inspecting agency.

Date of installation.

Manufacturer's name.

Installer's name.

FIELD QUALITY CONTROL

If required, inspection of penetration firestopping systems in this article is performed in accordance with ASTM E2174, "On-Site Inspection of Installed Fire Stops." To prevent conflicts of interest, ASTM E2174 precludes making Contractor responsible for engaging the testing agency. Inspectors may verify compliance by destructive examination of some completed installations.

Owner will engage a qualified testing agency to perform tests and inspections in accordance with ASTM E2174.

Where deficiencies are found or penetration firestopping system is damaged or removed because of testing, repair or replace penetration firestopping system to comply with requirements.

Proceed with enclosing penetration firestopping systems with other construction only after inspection reports are issued and installations comply with requirements.

CLEANING AND PROTECTION

Clean off excess fill materials adjacent to openings as the Work progresses by methods and with cleaning materials that are approved in writing by penetration firestopping system manufacturers and that do not damage materials in which openings occur.

Provide final protection and maintain conditions during and after installation that ensure that penetration firestopping systems are without damage or deterioration at time of Substantial Completion. If, despite such protection, damage or deterioration occurs, immediately cut out and remove damaged or deteriorated penetration firestopping material and install new materials to produce systems complying with specified requirements.

PENETRATION FIRESTOPPING SYSTEM SCHEDULE

Retain paragraphs in this schedule and revise to suit Project. Delete schedule if penetration firestopping systems are selected by Contractor.

Retain first paragraph below if UL-classified systems are required.

Where UL-classified systems are indicated, they refer to system numbers in UL's "Fire Resistance Directory" under product Category XHEZ.

Retain first paragraph below if Intertek Group-listed systems are required.

Where Intertek Group-listed systems are indicated, they refer to design numbers in Intertek Group's "Directory of Listed Building Products" under "Firestop Systems."

Retain first paragraph below if FM Approval-approved systems are required.

Where FM Approval-approved systems are indicated, they refer to design numbers listed in FM Approval's "Approval Guide" under "Wall and Floor Penetration Fire Stops."

Copy and re-edit remaining paragraphs for each system required. Coordinate with manufacturers specified in Part 2. If retaining FS option as means of identifying location of each firestopping system application on Drawings, insert drawing designation.

Each system designation is based on testing of proprietary products; for nonproprietary specifications, list multiple or a range of system designations for each condition, add basis-of-design products and comparable manufacturers, or specify each condition by rating requirements and fill material.

Penetration Firestopping Systems with No Penetrating Items <Insert drawing designation>:

Retain one or more of first three subparagraphs below if required. If retaining first subparagraph, retain one alpha-alpha option followed by either a four-digit number or range of four-digit numbers from 0001 to 0999. See the Evaluations for explanation of UL-system numbers.

HoldRite's "HydroFlame," "HydroFlame PRO," and "HydroFlame Custom Built" comply with the requirements of UL-Classified System C-AJ-0171.

UL-Classified Systems: [C-AJ-] [C-BJ-] [F-A-] [F-B-] [F-C-] [W-J-] [W-L-] <Insert four-digit number> [0001-0999].

Intertek Group-Listed Systems: <Insert design numbers>.

FM Approval-Approved Systems: <Insert design numbers>.

Retain one or more of six subparagraphs below if not retaining system designation subparagraphs above.

HoldRite's "HydroFlame," "HydroFlame PRO," and "HydroFlame Custom Built" provide an F-rating of 2 hours and a T-rating of 1-3/4 or 2 hours.

F-Rating: [1 hour] [2 hours] <Insert number of hours>.

T-Rating: [1 hour] [1-3/4 hours] [2 hours] <Insert number of hours>.

L-Rating at Ambient: Less than <Insert cfm/sq. ft. (cu. m/s per sq. m)>.

L-Rating at 400 Deg F (204 Deg C): Less than <Insert cfm/sq. ft. (cu. m/s per sq. m)>.

W-Rating: No leakage of water at completion of water-leakage testing.

Type of Fill Materials: [As required to achieve rating] <Insert material>.

Penetration Firestopping Systems for Metallic Pipes, Conduit, or Tubing <Insert drawing designation>:

Retain one or more of first three subparagraphs below if required. If retaining first subparagraph, retain one alpha-alpha option followed by either a four-digit number or range of four-digit numbers from 1001 to 1999. See the Evaluations for explanation of UL-system numbers.

HoldRite's "HydroFlame," "HydroFlame PRO," and "HydroFlame Custom Built" comply with the requirements of UL-Classified System F-C-1177; F-C-1178; and W-L-1179, -1180, -1181, -1182, -1183, -1574, -1558, -1561, -1565, -1566, -1568, and -1575.

UL-Classified Systems: [C-AJ-] [C-BJ-] [C-BK-] [F-A-] [F-B-] [F-C-] [F-E-] [W-J-] [W-K-] [W-L-] [W-N-] <Insert four-digit number> [1001-1999].

Intertek Group-Listed Systems: <Insert design number>.

FM Approval-Approved Systems: <Insert design number>.

Retain one or more of six subparagraphs below if not retaining system designation subparagraphs above.

F-Rating: [1 hour] [2 hours] <Insert number of hours>.

T-Rating: [1 hour] [2 hours] <Insert number of hours>.

L-Rating at Ambient: Less than <Insert cfm/sq. ft. (cu. m/s per sq. m)>.

L-Rating at 400 Deg F (204 Deg C): Less than <Insert cfm/sq. ft. (cu. m/s per sq. m)>.

W-Rating: No leakage of water at completion of water-leakage testing.

Type of Fill Materials: [As required to achieve rating] <Insert material>.

Penetration Firestopping Systems for Nonmetallic Pipe, Conduit, or Tubing <Insert drawing designation>:

Retain one or more of first three subparagraphs below if required. If retaining first subparagraph, retain one alpha-alpha option followed by either a four-digit number or range of four-digit numbers from 2001 to 2999. See the Evaluations for explanation of UL-system numbers.

UL-Classified Systems: [C-AJ-] [C-BJ-] [C-BK-] [F-A-] [F-B-] [F-C-] [F-E-] [W-J-] [W-K-] [W-L-] [W-N-] <Insert four-digit number> [2001-2999].

Intertek Group-Listed Systems: <Insert design number>.

FM Approval-Approved Systems: <Insert design number>.

Retain one or more of six subparagraphs below if not retaining system designation subparagraphs above.

F-Rating: [1 hour] [2 hours] <Insert number of hours>.

T-Rating: [1 hour] [2 hours] <Insert number of hours>.

L-Rating at Ambient: Less than <Insert cfm/sq. ft. (cu. m/s per sq. m)>.

L-Rating at 400 Deg F (204 Deg C): Less than <Insert cfm/sq. ft. (cu. m/s per sq. m)>.

W-Rating: No leakage of water at completion of water-leakage testing.

Type of Fill Materials: [As required to achieve rating] <Insert material>.

Penetration Firestopping Systems for Electrical Cables <Insert drawing designation>:

Retain one or more of first three subparagraphs below if required. If retaining first subparagraph, retain one alpha-alpha option followed by either a four-digit number or range of four-digit numbers from 3001 to 3999. See the Evaluations for explanation of UL-system numbers.

UL-Classified Systems: [C-AJ-] [C-BJ-] [C-BK-] [F-A-] [F-B-] [F-C-] [F-E-] [W-J-] [W-K-] [W-L-] <Insert four-digit number> [3001-3999].

Intertek Group-Listed Systems: <Insert design number>.

FM Approval-Approved Systems: <Insert design number>.

Retain one or more of six subparagraphs below if not retaining system designation subparagraphs above.

F-Rating: [1 hour] [2 hours] <Insert number of hours>.

T-Rating: [1 hour] [2 hours] <Insert number of hours>.

L-Rating at Ambient: Less than <Insert cfm/sq. ft. (cu. m/s per sq. m)>.

L-Rating at 400 Deg F (204 Deg C): Less than <Insert cfm/sq. ft. (cu. m/s per sq. m)>.

W-Rating: No leakage of water at completion of water-leakage testing.

Type of Fill Materials: [As required to achieve rating] <Insert material>.

Penetration Firestopping Systems for Cable Trays with Electric Cables <Insert drawing designation>:

Retain one or more of first three subparagraphs below if required. If retaining first subparagraph, retain one alpha-alpha option followed by either a four-digit number or range of four-digit numbers from 4001 to 4999. See the Evaluations for explanation of UL-system numbers.

UL-Classified Systems: [C-AJ-] [C-BJ-] [F-A-] [F-B-] [F-C-] [W-J-] [W-K-] [W-L-] <Insert four-digit number> [4001-4999].

Intertek Group-Listed Systems: <Insert design number>.

FM Approval-Approved Systems: <Insert design number>.

Retain one or more of six subparagraphs below if not retaining system designation subparagraphs above.

F-Rating: [1 hour] [2 hours] <Insert number of hours>.

T-Rating: [1 hour] [2 hours] <Insert number of hours>.

L-Rating at Ambient: Less than <Insert cfm/sq. ft. (cu. m/s per sq. m)>.

L-Rating at 400 Deg F (204 Deg C): Less than <Insert cfm/sq. ft. (cu. m/s per sq. m)>.

W-Rating: No leakage of water at completion of water-leakage testing.

Type of Fill Materials: [As required to achieve rating] <Insert material>.

Penetration Firestopping Systems for Insulated Pipes <Insert drawing designation>:

Retain one or more of first three subparagraphs below if required. If retaining first subparagraph, retain one alpha-alpha option followed by either a four-digit number or range of four-digit numbers from 5001 to 5999. See the Evaluations for explanation of UL-system numbers.

UL-Classified Systems: [C-AJ-] [C-BJ-] [C-BK-] [F-A-] [F-B-] [F-C-] [F-E-] [W-J-] [W-L-] [W-N-] <Insert four-digit number> [5001-5999].

Intertek Group-Listed Systems: <Insert design number>.

FM Approval-Approved Systems: <Insert design number>.

Retain one or more of six subparagraphs below if not retaining system designation subparagraphs above.

F-Rating: [1 hour] [2 hours] <Insert number of hours>.

T-Rating: [1 hour] [2 hours] <Insert number of hours>.

L-Rating at Ambient: Less than <Insert cfm/sq. ft. (cu. m/s per sq. m)>.

L-Rating at 400 Deg F (204 Deg C): Less than <Insert cfm/sq. ft. (cu. m/s per sq. m)>.

W-Rating: No leakage of water at completion of water-leakage testing.

Type of Fill Materials: [As required to achieve rating] <Insert material>.

Penetration Firestopping Systems for Miscellaneous Electrical Penetrants <Insert drawing designation>:

Retain one or more of first three subparagraphs below if required. If retaining first subparagraph, retain one alpha-alpha option followed by either a four-digit number or range of four-digit numbers from 6001 to 6999. See the Evaluations for explanation of UL-system numbers.

UL-Classified Systems: [C-AJ-] [C-BJ-] [F-A-] [W-L-] [W-J-] <Insert four-digit number> [6001-6999].

Intertek Group-Listed Systems: <Insert design number>.

FM Approval-Approved Systems: <Insert design number>.

Retain one or more of six subparagraphs below if not retaining system designation subparagraphs above.

F-Rating: [1 hour] [2 hours] <Insert number of hours>.

T-Rating: [1 hour] [2 hours] <Insert number of hours>.

L-Rating at Ambient: Less than <Insert cfm/sq. ft. (cu. m/s per sq. m)>.

L-Rating at 400 Deg F (204 Deg C): Less than <Insert cfm/sq. ft. (cu. m/s per sq. m)>.

W-Rating: No leakage of water at completion of water-leakage testing.

Type of Fill Materials: [As required to achieve rating] <Insert material>.

Penetration Firestopping Systems for Miscellaneous Mechanical Penetrants <Insert drawing designation>:

Retain one or more of first three subparagraphs below if required. If retaining first subparagraph, retain one alpha-alpha option followed by either a four-digit number or range of four-digit numbers from 7001 to 7999. See the Evaluations for explanation of UL-system numbers.

UL-Classified Systems: [C-AJ-] [C-BJ-] [F-A-] [F-B-] [F-C-] [F-E-] [W-J-] [W-L-] [W-N-] <Insert four-digit number> [7001-7999].

Intertek Group-Listed Systems: <Insert design number>.

FM Approval-Approved Systems: <Insert design number>.

Retain one or more of six subparagraphs below if not retaining system designation subparagraphs above.

F-Rating: [1 hour] [2 hours] <Insert number of hours>.

T-Rating: [1 hour] [2 hours] <Insert number of hours>.

L-Rating at Ambient: Less than <Insert cfm/sq. ft. (cu. m/s per sq. m)>.

L-Rating at 400 Deg F (204 Deg C): Less than <Insert cfm/sq. ft. (cu. m/s per sq. m)>.

W-Rating: No leakage of water at completion of water- leakage testing.

Type of Fill Materials: [As required to achieve rating] <Insert material>.

Penetration Firestopping Systems for Groupings of Penetrants <Insert drawing designation>:

Retain one or more of first three subparagraphs below if required. If retaining first subparagraph, retain one alpha-alpha option followed by either a four-digit number or range of four-digit numbers from 8001 to 8999. See the Evaluations for explanation of UL-system numbers.

UL-Classified Systems: [C-AJ-] [C-BJ-] [F-A-] [F-B-] [F-C-] [F-E-] [W-J-] [W-L-] <Insert four-digit number> [8001-8999].

Intertek Group-Listed Systems: <Insert design number>.

FM Approval-Approved Systems: <Insert design number>.

Retain one or more of six subparagraphs below if not retaining system designation subparagraphs above.

F-Rating: [1 hour] [2 hours] <Insert number of hours>.

T-Rating: [1 hour] [2 hours] <Insert number of hours>.

L-Rating at Ambient: Less than <Insert cfm/sq. ft. (cu. m/s per sq. m)>.

L-Rating at 400 Deg F (204 Deg C): Less than <Insert cfm/sq. ft. (cu. m/s per sq. m)>.

W-Rating: No leakage of water at completion of water-leakage testing.

Type of Fill Materials: [As required to achieve rating] <Insert material>.

END OF SECTION 078413