Copyright 2017 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

This Product MasterSpec Section is licensed by Deltek, Inc. to HoldRite; Division of Reliance Worldwide Corporation ("Licensee").

This Product MasterSpec Section modifies the original MasterSpec text and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, Deltek or The American Institute of Architects (AIA). Neither AIA nor Deltek are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user. A qualified design professional should review and edit the document to suit project requirements.

For more information, contact HoldRite; Division of Reliance Worldwide Corporation, 2300 Defoor Hills NW, Atlanta, GA 30318; Phone: (800) 321-0316 | (760) 744-6944; Fax: (760) 744-0507; Website: www.holdrite.com; Email: sales@holdrite.com.

For information about MasterSpec, contact Deltek at (800) 424-5080 or visit masterspec.com.

SECTION 220529 - HANGERS AND SUPPORTS FOR PLUMBING PIPING AND EQUIPMENT

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Access Product MasterSpec Sections:

<Double click here to view the list of manufacturer Sections available at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

Metal pipe hangers and supports.

Trapeze pipe hangers.

Fiberglass pipe hangers.

Metal framing systems.

Fiberglass strut systems.

Thermal hanger-shield inserts.

Fastener systems.

Pipe stands.

Pipe-positioning systems.

Equipment supports.

Acoustical pipe isolation.

Seismic equipment restraints.

Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Section 055000 "Metal Fabrications" for structural-steel shapes and plates for trapeze hangers for pipe and equipment supports.

Section 220516 "Expansion Fittings and Loops for Plumbing Piping" for pipe guides and anchors.

[Section 220548 "Vibration and Seismic Controls for Plumbing Piping and Equipment"] [Section 220548.13 "Vibration Controls for Plumbing Piping and Equipment"] for vibration isolation devices.

DEFINITIONS

MFMA: Metal Framing Manufacturers Association.

MSS: Manufacturers Standardization Society of The Valve and Fittings Industry Inc.

ACTION SUBMITTALS

Product Data: For each type of product.

Shop Drawings: Include fabrication and installation details for the following:

Trapeze pipe hangers.

Metal framing systems.

Fiberglass strut systems.

Pipe stands.

Equipment supports.

Pipe positioning systems.

Acoustical pipe isolation supports.

Seismic equipment restraints.

INFORMATIONAL SUBMITTALS

Retain "Welding certificates" Paragraph below if retaining "Structural-Steel Welding Qualifications" Paragraph and "Pipe Welding Qualifications" Paragraph in "Quality Assurance" Article.

Welding certificates.

QUALITY ASSURANCE

Retain both "Structural-Steel Welding Qualifications" Paragraph and "Pipe Welding Qualifications" Paragraph below if shop or field welding is required. If retaining, also retain "Welding certificates" Paragraph in "Informational Submittals" Article.

Structural-Steel Welding Qualifications: Qualify procedures and personnel in accordance with AWS D1.1/D1.1M.

Pipe Welding Qualifications: Qualify procedures and operators in accordance with 2015 ASME Boiler and Pressure Vessel Code, Section IX.

PRODUCTS

Manufacturers and products listed in SpecAgent and MasterWorks Paragraph Builder are neither recommended nor endorsed by the AIA or Deltek. Before inserting names, verify that manufacturers and products listed there comply with requirements retained or revised in descriptions and are both available and suitable for the intended applications. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

PERFORMANCE REQUIREMENTS

Structural Performance: Hangers and supports for plumbing piping and equipment shall withstand the effects of gravity loads and stresses within limits and under conditions indicated in accordance with [ASCE/SEI 7] <Insert requirement>.

Design supports for multiple pipes, including pipe stands, capable of supporting combined weight of supported systems, system contents, and test water.

Design equipment supports capable of supporting combined operating weight of supported equipment and connected systems and components.

Design seismic-restraint hangers and supports for piping and equipment[ and obtain approval from authorities having jurisdiction].

METAL PIPE HANGERS AND SUPPORTS

Carbon-Steel Pipe Hangers and Supports:

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

For HoldRite's "Stout Bracket Telescoping Supports," see https://HoldRite.com/products/telescoping-supports/stout-bracket-telescoping-supports/stout-bracket-galvanized-brackets/.

For HoldRite's "EZ-Strut Overhead Supports," see https://HoldRite.com/products/overhead-supports/ez-strut-overhead-supports/.

For HoldRite's "PexRite PEX Supports," see https://HoldRite.com/products/pex-supports/pexrite-pex-supports/.

For HoldRite's "ProGuard Pipe Supports," see https://HoldRite.com/products/pex-supports/HoldRite-proguard-pex-supports/.

For HoldRite's "LockRite CPVC Pipe Supports," see https://HoldRite.com/products/cpvc-supports/lockrite-cpvc/.

For HoldRite's "HoldRite Brackets and Supports," see https://HoldRite.com/products/overhead-supports/HoldRite-overhead-supports/.

For HoldRite's "HoldRite Silencer Acoustic Isolation Hangers/Clamps/Inserts," see https://HoldRite.com/products/acoustic-isolation/silencer/.

Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of Reliance Worldwide Corporation; [Stout Bracket Telescoping Supports] [EZ-Strut Overhead Supports] [PexRite PEX Supports] [ProGuard Pipe Supports] [LockRite CPVC Pipe Supports] [HoldRite Brackets and Supports] [HoldRite Silencer Acoustic Isolation Hangers/Clamps/Inserts] or comparable product.

Description: MSS SP-58, Types 1 through 58, factory-fabricated components.

Galvanized Metallic Coatings: Pregalvanized, hot-dip galvanized, or electro-galvanized.

Nonmetallic Coatings: Plastic coated or epoxy powder coated.

Padded Hangers: Hanger with fiberglass or other pipe insulation pad or cushion to support bearing surface of piping.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product. For HoldRite's "HoldRite Silencer Acoustic Isolation Hangers/Clamps/Inserts," see https://HoldRite.com/products/acoustic-isolation/silencer/.

Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of Reliance Worldwide Corporation; HoldRite Silencer Acoustic Isolation Hangers/Clamps/Inserts or comparable product.

Hanger Rods: Continuous-thread rod, nuts, and washer made of [carbon steel] [stainless steel] <Insert material>.

Stainless Steel Pipe Hangers and Supports:

Description: MSS SP-58, Types 1 through 58, factory-fabricated components.

Padded Hangers: Hanger with fiberglass or other pipe insulation pad or cushion to support bearing surface of piping.

Strut-Mounted Pipe Clamps:

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of Reliance Worldwide Corporation; HoldRite #100 and #200 Series Cushion Clamps with Stainless Steel Frames or comparable product.

Hanger Rods: Continuous-thread rod, nuts, and washer made of [stainless steel] <Insert material>.

Copper Pipe and Tube Hangers:

Description: MSS SP-58, Types 1 through 58, copper-coated-steel, factory-fabricated components.

Padded Hangers: Hanger with CPVC pipe insulation pad or cushion to support bearing surface of piping.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of Reliance Worldwide Corporation; [HoldRite Silencer Loop and J-Hangers] [HoldRite Strut Clamps] or comparable product.

Hanger Rods: Continuous-thread rod, nuts, and washer made of [copper-coated steel] [stainless steel] <Insert material>.

No-Hub Cast Iron Soil Pipe Fitting Restraints:

Description: CISPI Designation 301-18 and 310-18, large-diameter no-hub cast iron fittings, over 4 inches (100 mm) in size, shall be provided with supplemental support to minimize the risk of joint separation under high-thrust conditions. Auxiliary restraint products used shall be manufactured assemblies with thrust pressure rating adequate for the specific installation. Field-devised methods and materials shall not be used to accomplish this application solution.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product. For HoldRite's "#117 Series No-Hub Fitting Restraints," see https://HoldRite.com/products/no-hub-fitting-restraints/.

Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of Reliance Worldwide Corporation; #117 Series No-Hub Fitting Restraints or comparable product.

TRAPEZE PIPE HANGERS

Trapeze pipe hanger in "Description" Paragraph below requires calculating and detailing at each use.

Description: MSS SP-58, Type 59, shop- or field-fabricated pipe-support assembly, made from structural-carbon-steel shapes, with MSS SP-58 carbon-steel hanger rods, nuts, saddles, and washers. The total load of piping components imposed on trapeze spans shall not exceed manufacturer's design load rating. Load calculation and detail of each unit shall include a safety factor of two times the expected load.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

For HoldRite's "EZ-Strut Overhead Supports," see https://HoldRite.com/products/overhead-supports/ez-strut-overhead-supports/.

For HoldRite's "Strut-Mounted Cushion Clamps," see https://HoldRite.com/products/overhead-supports/strut-mounted-cushion-clamps/.

For HoldRite's "Insulation Couplings," see https://HoldRite.com/products/overhead-supports/insulation-couplings-overhead-supports/.

Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of Reliance Worldwide Corporation; [EZ-Strut Overhead Supports] [Strut-Mounted Cushion Clamps] [Insulation Couplings] or comparable product.

HoldRite does not manufacture products complying with requirements of "Fiberglass Pipe Hangers" Article below.

FIBERGLASS PIPE HANGERS

Clevis-Type, Fiberglass Pipe Hangers:

Description: Similar to MSS SP-58, Type 1 steel pipe hanger, except hanger is made of fiberglass or fiberglass-reinforced resin.

Hanger rods for fiberglass pipe hangers in "Hanger Rods" Subparagraph below are typically stainless steel.

Hanger Rods: Continuous-thread rod, washer, and nuts made of [fiberglass] [polyurethane] [or] [stainless steel] <Insert material>.

Retain "Flammability" Subparagraph below if retaining "fiberglass" or "polyurethane" option in "Hanger Rods" Subparagraph above.

Flammability: ASTM D635, ASTM E84, UL 94.

Strap-Type, Fiberglass Pipe Hangers:

Description: Similar to MSS SP-58, Type 9 or Type 10 steel pipe hanger, except hanger is made of fiberglass-reinforced resin.

Flammability: ASTM D635, ASTM E84, UL 94.

Hanger rods and attachments in "Hanger Rod and Fittings" Subparagraph below are typically stainless steel.

Hanger Rod and Fittings: Continuous-thread rod, washer, and nuts made of [stainless steel] <Insert material>.

METAL FRAMING SYSTEMS

Framing systems in "MFMA Manufacturer Metal Framing Systems" Paragraph below are made by MFMA members.

MFMA Manufacturer Metal Framing Systems:

Retain "Manufacturers" Subparagraph below and list of manufacturers to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Cooper B-line.

Flex-Strut Inc.

G-Strut.

Haydon Corporation.

Powerstrut Corporation.

Thomas & Betts Corporation; A Member of the ABB Group.

Unistrut; Part of Atkore International.

Wesanco, Inc.

<Insert manufacturer's name>.

Description: Shop- or field-fabricated pipe-support assembly, made of steel channels, accessories, fittings, and other components for supporting multiple parallel pipes.

Standard: Comply with MFMA-4, factory-fabricated components for field assembly.

Channels: Continuous slotted [carbon-steel] [stainless steel, Type 304] [stainless steel, Type 316] [extruded-aluminum] <Insert material> channel with inturned lips.

Channel Width: Selected for applicable load criteria.

Channel Nuts: Formed or stamped nuts or other devices designed to fit into channel slot and, when tightened, prevent slipping along channel.

Hanger Rods: Continuous-thread rod, nuts, and washer made of [carbon steel] [stainless steel] <Insert material>.

Retain "Metallic Coating," "Paint Coating," "Plastic Coating," or "Combination Coating" Subparagraph below for coating. Coordinate coating with material retained in "Channels" Subparagraph above.

Metallic Coating: [No coating] [Plain] [Pregalvanized G90 (Z275)] [Electroplated zinc] [Hot-dip galvanized] [Gold (yellow zinc dichromate) galvanized].

Paint Coating: [Green epoxy, acrylic, or urethane] <Insert paint type>.

Plastic Coating: [PVC] <Insert plastic type>.

Combination Coating: <Insert coating materials in order of application>.

Non-MFMA Manufacturer Metal Framing Systems:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

For HoldRite's "HoldRite Brackets and Supports," see https://HoldRite.com/products/overhead-supports/HoldRite-overhead-supports/.

For HoldRite's "Stout Bracket Telescoping Supports," see https://HoldRite.com/products/telescoping-supports/stout-bracket-telescoping-supports/stout-bracket-galvanized-brackets/.

For HoldRite's "EZ-Strut Overhead Supports," see https://HoldRite.com/products/overhead-supports/ez-strut-overhead-supports/.

          - Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of Reliance Worldwide Corporation; [HoldRite Brackets and Supports] [Stout Bracket Telescoping Supports] [EZ-Strut Overhead Supports] or comparable product by one of the following:

Anvil International.

CADDY; a brand of nVent.

Carpenter & Paterson, Inc.

Empire Industries, Inc.

FNW; Ferguson Enterprises, Inc.

Gripple Inc.

MIRO Industries.

PHD Manufacturing, Inc.

Rooftop Support Systems, a division of Eberl Iron Works, Inc.

Sioux Chief Manufacturing Company, Inc.

<Insert manufacturer's name>.

Description: Shop- or field-fabricated pipe-support assembly, made of steel sheet, bands, channels, accessories, fittings, and other components for supporting multiple parallel pipes.

Standard: Comply with MFMA-4, factory-fabricated components for field assembly.

Channels: Continuous slotted [carbon-steel] [copper-bonded steel] [galvanized-steel] [stainless steel] <Insert material> channel with inturned lips.

            - Sheet Metal Thickness: 0.0598 inch (1.5189 mm), 16 gauge.

Channel Width: Select for applicable load criteria.

Channel Nuts: Formed or stamped nuts or other devices designed to fit into channel slot and, when tightened, prevent slipping along channel.

Pipe Inserts and Clamps: UPC-IPC-IAPMO listed, kynar flex, nylon, polyethylene, or [glass-filled ]polypropylene [variable-closure ]strut clamps.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product.

Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of Reliance Worldwide Corporation; [HoldRite Strut Clamps] [EZ-Strut Clamps] [Strut-Mounted Cushion Clamps] [HoldRite #72 and #82 Series Insulation Coupling Clamps] or comparable product.

Hanger Rods: Continuous-thread rod, nuts, and washer made of [carbon steel] [stainless steel] <Insert material>.

Retain "Metallic Coating," "Paint Coating," or "Plastic Coating" Subparagraph below for coating. Coordinate coating with material retained in "Channels" Subparagraph above.

Metallic Coating: [No coating] [Plain] [Pregalvanized G90 (Z275)] [Hot-dip galvanized]

Paint Coating: [Green epoxy, acrylic, or urethane] <Insert paint coating>.

Plastic Coating: [PVC] <Insert plastic type>.

HoldRite does not manufacture products complying with requirements of "Fiberglass Strut Systems" Article below.

FIBERGLASS STRUT SYSTEMS

Fiberglass strut systems in this article require calculating and detailing at each use.

Retain "Manufacturers" Paragraph below and list of manufacturers to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Champion Fiberglass, Inc.

Fabco Plastics Wholesale Limited.

G-Strut.

Seasafe, Inc.; AMICO, a Gibraltar Industries Company.

Unistrut; Part of Atkore International.

<Insert manufacturer's name>.

Description: Structural-grade, factory-formed, glass-fiber-resin channels and angles for supporting multiple parallel pipes.

Standard: Comply with MFMA-4, factory-fabricated components for field assembly.

Channels: Continuous slotted fiberglass-reinforced plastic channel with inturned lips.

Channel Width: Selected for applicable load criteria.

Fittings and Accessories: Products provided by channel and angle manufacturer and designed for use with those items.

Fitting and Accessory Materials: Same as those for channels and angles[, except metal items may be stainless steel].

Rated Strength: Selected to suit applicable load criteria.

Protect finishes on exposed surfaces from damage by applying a strippable, temporary protective covering before shipping.

THERMAL HANGER-SHIELD INSERTS

Retain "Basis-of-Design Product" Paragraph below to require a specific product or a comparable product from other manufacturers.

For HoldRite's "Insulation Couplings - Steel Strut Clamps," see https://holdrite.com/products/overhead-supports/insulation-couplings-overhead-supports/insulation-couplings-steel-strut-clamp/.

For HoldRite's "Insulation Couplings - Plastic Strut Clamps," see https://holdrite.com/products/overhead-supports/insulation-couplings-overhead-supports/insulation-couplings-plastic-strut-clamp/.

For HoldRite's "Insulation Couplings - Clevis Hangers," see https://holdrite.com/products/overhead-supports/insulation-couplings-overhead-supports/insulation-couplings-clevis-hanger/.

Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of Reliance Worldwide Corporation; [Insulation Couplings - Steel Strut Clamps] [Insulation Couplings - Plastic Strut Clamps] [Insulation Couplings - Clevis Hangers] or comparable product by one of the following.

Buckaroos, Inc.

CADDY; a brand of nVent.

Carpenter & Paterson, Inc.

Clement Support Services.

National Pipe Hanger Corporation.

Pipe Shields Inc.

Piping Technology & Products, Inc.

Rilco Manufacturing Co., Inc.

Value Engineered Products, Inc.

<Insert manufacturer's name>.

Insulation-Insert Material for Cold Piping: [ASTM C552, Type II cellular glass with 100-psig (688-kPa)] [or] [ASTM C591, Type VI, Grade 1 polyisocyanurate with 125-psig (862-kPa)] minimum compressive strength and vapor barrier.

Insulation-Insert Material for Hot Piping: [Water-repellent-treated, ASTM C533, Type I calcium silicate with 100-psig (688-kPa)] [ASTM C552, Type II cellular glass with 100-psig (688-kPa)] [or] [ASTM C591, Type VI, Grade 1 polyisocyanurate with 125-psig (862-kPa)] minimum compressive strength.

For Trapeze or Clamped Systems: Insert and shield shall cover entire circumference of pipe.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of Reliance Worldwide Corporation; HoldRite #72 and #82 Series Insulation Coupling Strut Clamps or comparable product.

For Clevis or Band Hangers: Insert and shield shall cover lower 180 degrees of pipe.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of Reliance Worldwide Corporation; HoldRite #70 Series Insulation Coupling Clevis Hangers or comparable product.

Insert Length: Extend 2 inches (50 mm) beyond sheet metal shield for piping operating below ambient air temperature.

FASTENER SYSTEMS

Verify suitability of fasteners in this article for use in lightweight concrete or concrete slabs less than 4 inches (100 mm) thick. Powder-actuated fasteners may be banned for use in certain occupancies. Consult authorities having jurisdiction and Owner's project requirements.

Powder-Actuated Fasteners: Threaded-steel stud, for use in hardened portland cement concrete, with pull-out, tension, and shear capacities appropriate for supported loads and building materials where used.

Retain "Manufacturers" Subparagraph below and list of manufacturers to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Hilti, Inc.

ITW Ramset/Red Head; Illinois Tool Works, Inc.

MKT Fastening, LLC.

Simpson Strong-Tie Co., Inc.

<Insert manufacturer's name>.

Mechanical-Expansion Anchors: Insert-wedge-type anchors, for use in hardened portland cement concrete, with pull-out, tension, and shear capacities appropriate for supported loads and building materials where used.

Retain "Manufacturers" Subparagraph below and list of manufacturers to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

B-line, an Eaton business.

Empire Tool and Manufacturing Co., Inc.

Hilti, Inc.

ITW Ramset/Red Head; Illinois Tool Works, Inc.

MKT Fastening, LLC.

<Insert manufacturer's name>.

Indoor Applications: [Zinc-coated] [or] [stainless] steel.

Outdoor Applications: Stainless steel.

        - Cast-In-Place Anchors: Steel or malleable concrete inserts for use with NPS 1 (DN 25) pipe and tubing or smaller, hung high and tight to structure above. Comply with MSS SP-58 load rating.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of Reliance Worldwide Corporation; HoldRite #125 Series Hangover Brackets or comparable product.

PIPE STANDS

Pipe stands in this article require calculating and detailing at each use.

General Requirements for Pipe Stands: Shop- or field-fabricated assemblies made of manufactured corrosion-resistant components to support roof-mounted piping.

Compact Pipe Stand:

Description: Single base unit with integral-rod roller, pipe clamps, or V-shaped cradle to support pipe, for roof installation without membrane penetration.

Base: Single, vulcanized rubber, molded polypropylene, or polycarbonate.

Retain "Recycled Content" Subparagraph below to specify recycled content if required. An alternative method of requiring recycled content is to retain requirement in Project's Division 01 sustainable design requirements Section that gives Contractor the option and responsibility to determine how recycled content requirements will be met.

Recycled Content: Postconsumer recycled content plus one-half of preconsumer recycled content not less than <Insert number> percent.

Hardware: Galvanized steel or polycarbonate.

Accessories: Protection pads.

Low-Profile, Single-Base, Single-Pipe Stand:

Description: Single base with vertical and horizontal members, and pipe support, for roof installation without membrane protection.

Base: Single, vulcanized rubber, molded polypropylene, or polycarbonate.

Retain "Recycled Content" Subparagraph below to specify recycled content if required. An alternative method of requiring recycled content is to retain requirement in Project's Division 01 sustainable design requirements Section that gives Contractor the option and responsibility to determine how recycled content requirements will be met.

Recycled Content: Postconsumer recycled content plus one-half of preconsumer recycled content not less than <Insert number> percent.

Vertical Members: Two [galvanized] [stainless]-steel, continuous-thread, 1/2-inch (12-mm) rods.

Horizontal Member: Adjustable horizontal, [galvanized] [stainless]-steel pipe support channels.

Pipe Supports: [Roller] [Strut clamps] [Clevis hanger] [Swivel hanger].

Hardware: [Galvanized] [Stainless] steel.

Accessories: Protection pads.

Height: [12 inches (300 mm) above roof] <Insert lesser dimension above roof>.

High-Profile, Single-Base, Single-Pipe Stand:

Description: Single base, vertical and horizontal members, and pipe support, for roof installation without membrane penetration.

Base: Single vulcanized rubber or molded polypropylene.

Retain "Recycled Content" Subparagraph below to specify recycled content if required. An alternative method of requiring recycled content is to retain requirement in Project's Division 01 sustainable design requirements Section that gives Contractor the option and responsibility to determine how recycled content requirements will be met.

Recycled Content: Postconsumer recycled content plus one-half of preconsumer recycled content not less than <Insert number> percent.

Vertical Members: Two [galvanized] [stainless]-steel, continuous-thread, 1/2-inch (12-mm) rods.

Horizontal Member: One adjustable-height, [galvanized-] [or] [stainless]-steel, pipe-support slotted channel or plate.

Pipe Supports: [Roller] [Clevis hanger] [Swivel hanger].

Hardware: [Galvanized] [Stainless] steel.

Retain first or second option in "Accessories" Subparagraph below if retaining "Clevis hanger" or "Swivel hanger" option in "Pipe Supports" Subparagraph above.

Accessories: Protection pads[, 1/2-inch (12-mm), continuous-thread, galvanized-steel rod] [, 1/2-inch (12-mm), continuous-thread, stainless steel rod].

Height: [36 inches (900 mm) above roof] <Insert lesser dimension above roof>.

High-Profile, Multiple-Pipe Stand:

Description: Assembly of bases, vertical and horizontal members, and pipe supports, for roof installation without membrane penetration.

Bases: Two or more; [vulcanized rubber] [molded polypropylene] <Insert material>.

Retain "Recycled Content" Subparagraph below to specify recycled content if required. An alternative method of requiring recycled content is to retain requirement in Project's Division 01 sustainable design requirements Section that gives Contractor the option and responsibility to determine how recycled content requirements will be met.

Recycled Content: Postconsumer recycled content plus one-half of preconsumer recycled content not less than <Insert number> percent.

Vertical Members: Two or more, [galvanized] [stainless]-steel channels.

Horizontal Members: One or more, adjustable-height, [galvanized] [stainless]-steel pipe support.

Pipe Supports: [Roller] [Strut clamps] [Clevis hanger] [Swivel hanger].

Hardware: [Galvanized] [Stainless] steel.

Retain option in "Accessories" Subparagraph below if retaining "Clevis hanger" or "Swivel hanger" option in "Pipe Supports" Subparagraph above.

Accessories: Protection pads[, 1/2-inch (12-mm), continuous-thread rod].

Height: [36 inches (900 mm) above roof] <Insert lesser dimension above roof>.

Curb-Mounted-Type Pipe Stands: Shop- or field-fabricated pipe supports made from structural-steel shapes, continuous-thread rods, and rollers, for mounting on permanent stationary roof curb.

PIPE-POSITIONING SYSTEMS

Description: IAPMO PS 42 positioning system composed of metal brackets, clips, and straps for positioning piping in pipe spaces; for plumbing fixtures in commercial applications.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of Reliance Worldwide Corporation; [Stout Bracket Telescoping Supports] [EZ-Strut Overhead Supports] [PexRite PEX Supports] [ProGuard Pipe Supports] [LockRite CPVC Pipe Supports] [HoldRite Brackets and Supports] [HoldRite Silencer Acoustic Isolation Clamps/Inserts] or comparable product by one of the following:

C&S Mfg. Corp.

Samco Stamping, Inc.

<Insert manufacturer's name>.

EQUIPMENT SUPPORTS

Equipment support in "Description" Paragraph below requires calculating and detailing at each use.

Description: Welded, shop- or field-fabricated equipment support made from structural-carbon-steel shapes.

        - Factory-Manufactured Equipment Stands for Water Heaters.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of Reliance Worldwide Corporation; HoldRite Quickstand or comparable product.

        - Factory-Manufactured Equipment Platforms for Suspended Water Heaters and Similar Equipment.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of Reliance Worldwide Corporation; HoldRite Quickstand or comparable product.

Retain first paragraph below when water heater restraints are required in seismic zones.

        - Factory-Manufactured Water Heater Restraints: Comply with requirements of authorities having jurisdiction.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of Reliance Worldwide Corporation; [HoldRite Quickstrap] [HoldRite Quickstrap Deluxe] [HoldRite Quickbelt] or comparable product.

        - Factory-Manufactured Equipment Support for Thermal Expansion Tanks Mounted to Walls, Ceilings, or Similar surfaces.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of Reliance Worldwide Corporation; HoldRite Quickstrap or comparable product.

      - ACCESSORY PRODUCTS

        - Vertical Mid-Span Piping Supports: For use with vertically installed water, waste, vent, [air,] [medical gas,] [and] [fuel gas] pipe, NPS 4 (DN 100) and smaller, for a distance exceeding 48 inches (1.2 m).

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of Reliance Worldwide Corporation; HoldRite Stout Bracket Telescoping Supports or comparable product.

        - Plenum-Rated Support System: For use in supporting tubing and piping in plenum-rated applications. Maximum flame spread 25, smoke developed 50, when tested in accordance with ASTM E84.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of Reliance Worldwide Corporation; HoldRite Flame Fighter Series Clamps or comparable product.

        - Abrasion-Protection Isolators: Use for prevention of damage to tubes and piping caused by abrasion when passing through or in contact with studs, joists, and similar framing.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of Reliance Worldwide Corporation; [HoldRite #200 Series Isolators and Clamps] [HoldRite #400 Series Isolators] [HoldRite #300 Series Loop and J-Hangers] or comparable product.

        - Dissimilar Metal Isolators: Use for prevention of damage to tubes and pipes caused by contact between dissimilar metals.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of Reliance Worldwide Corporation; [HoldRite #200 Series Isolators and Clamps] [HoldRite #400 Series Isolators] [HoldRite #300 Series Loop and J-Hangers] [HoldRite #70, #72, #78 Series Insulation Couplings] [HoldRite #100 and #200 Series Cushion Clamps] or comparable product.

      - ACOUSTICAL NOISE AND VIBRATION ISOLATION

        - Acoustical Isolation System: Consisting of loop hangers, J-hangers, through-stud isolators, pipe clamps, riser clamp pads, neoprene and felt lining material, associated support bracketry, and firestop sleeve devices. For applications requiring acoustical isolation of tubing, piping, and equipment from building elements, such as floors, walls, and framing members.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product or a comparable product.

          - Basis-of-Design Product: Subject to compliance with requirements, provide HoldRite, Division of Reliance Worldwide Corporation; [HoldRite Silencer Acoustic Isolation Hangers/Clamps/Inserts used with Stout Bracket Telescoping Supports] [HoldRite HydroFlame Firestop Sleeve Devices] [HoldRite HydroFlame Firestop and Acoustic Sealants] or comparable product.

MATERIALS

Aluminum: ASTM B221 (ASTM B221M).

Carbon Steel: ASTM A1011/A1011M.

Structural Steel: ASTM A36/A36M carbon-steel plates, shapes, and bars; black and galvanized.

Stainless Steel: ASTM A240/A240M.

Grout: ASTM C1107/C1107M, factory-mixed and -packaged, dry, hydraulic-cement, nonshrink and nonmetallic grout; suitable for interior and exterior applications.

Properties: Nonstaining, noncorrosive, and nongaseous.

Design Mix: 5000-psi (34.5-MPa), 28-day compressive strength.

EXECUTION

APPLICATION

Comply with requirements in Section 078413 "Penetration Firestopping" for firestopping materials and installation, for penetrations through fire-rated walls, ceilings, and assemblies.

Strength of Support Assemblies: Where not indicated, select sizes of components, so strength will be adequate to carry present and future static loads within specified loading limits. Minimum static design load used for strength determination shall be weight of supported components plus [200 lb (90 kg)] <Insert value>.

HANGER AND SUPPORT INSTALLATION

Support of piping and equipment shall be by means of engineered products designed for each application. Comply with manufacturer's design load capacities. Makeshift, field-devised methods such as use of scrap materials, plumber's tape, tie wires, and similar methods are not permitted.

Metal Pipe-Hanger Installation: Comply with MSS SP-58. Install hangers, supports, clamps, and attachments as required to properly support piping from building structure.

Trapeze pipe hanger in "Metal Trapeze Pipe-Hanger Installation" Paragraph below requires calculating and detailing at each use.

Metal Trapeze Pipe-Hanger Installation: Comply with MSS SP-58. Arrange for grouping of parallel runs of horizontal piping, and support together on field-fabricated trapeze pipe hangers.

Pipes of Various Sizes: Support together and space trapezes for smallest pipe size, or install intermediate supports for smaller-diameter pipes as specified for individual pipe hangers.

For applications not suited to, or exceeding the capacity of, manufactured supports, field fabricate from ASTM A36/A36M carbon-steel shapes selected for loads being supported. Weld steel in accordance with AWS D1.1/D1.1M.

Fiberglass Pipe-Hanger Installation: Comply with applicable portions of MSS SP-58. Install hangers and attachments as required to properly support piping from building structure.

Framing system in first paragraph below requires calculating and detailing at each use.

[Metal] [Fiberglass ]Framing System Installation: Arrange for grouping of parallel runs of piping, and support together on field-assembled metal framing systems.

Thermal Hanger-Shield Installation: Install in pipe hanger or shield for insulated piping.

Fastener System Installation:

Verify suitability of fasteners in two subparagraphs below for use in lightweight concrete or concrete slabs less than 4 inches (100 mm) thick.

Install powder-actuated fasteners for use in lightweight concrete or concrete slabs less than 4 inches (100 mm) thick in concrete, after concrete is placed and completely cured. Use operators that are licensed by powder-actuated tool manufacturer. Install fasteners in accordance with powder-actuated tool manufacturer's operating manual.

Install mechanical-expansion anchors in concrete, after concrete is placed and completely cured. Install fasteners in accordance with manufacturer's written instructions.

Pipe stand in "Pipe Stand Installation" Paragraph below requires calculating and detailing at each use.

Pipe Stand Installation:

Pipe Stand Types, except Curb-Mounted Type: Assemble components and mount on smooth roof surface. Do not penetrate roof membrane.

Curb-Mounted-Type Pipe Stands: Assemble components or fabricate pipe stand and mount on permanent, stationary roof curb. See Section 077200 "Roof Accessories" for curbs.

Pipe-Positioning-System Installation: Install support devices to make rigid supply and waste piping connections to each plumbing fixture with the use of manufactured products, designed for each specific application. Makeshift, field-devised methods shall not be employed.

Install hangers and supports complete with necessary attachments, inserts, bolts, rods, nuts, washers, and other accessories with the use of manufactured products, designed for each specific application. Makeshift, field-devised methods shall not be employed.

Equipment support in "Equipment Support Installation" Paragraph below requires calculating and detailing at each use.

Equipment Support Installation: Use manufactured equipment supports designed for and recommended by manufacturer for specific applications. Comply with manufacturer's rated load capacities. For applications not suited to, or exceeding the capacity of, manufactured supports, fabricate supports from welded-structural-steel shapes.

Install hangers and supports to allow controlled thermal and seismic movement of piping systems, to permit freedom of movement between pipe anchors, and to facilitate action of expansion joints, expansion loops, expansion bends, and similar units.

Install lateral bracing with pipe hangers and supports to prevent swaying.

In compliance with U.S. soil pipe and fitting manufacturers' installation instructions, CISPI Designation 301-18 and 310-18, and CISPI Cast Iron Soil Pipe Handbook, regarding auxiliary support for no-hub cast iron pipe and fitting joints over 4 inches (100 mm) in size and for joints subjected to excessive thrust forces, use manufactured assemblies with appropriate thrust pressure ratings, rather than field-assembled miscellaneous materials.

Install building attachments within concrete slabs or attach to structural steel. Install additional attachments at concentrated loads, including valves, flanges, and strainers, [NPS 2-1/2 (DN 65)] <Insert size> and larger and at changes in direction of piping. Install concrete inserts before concrete is placed; fasten inserts to forms, and install reinforcing bars through openings at top of inserts.

For overhead pipe NPS 1 (DN 25) and smaller, use cast-in-place anchors specified herein.

Load Distribution: Install hangers and supports, so that piping live and dead loads and stresses from movement will not be transmitted to connected equipment.

Pipe Slopes: Install hangers and supports to provide indicated pipe slopes and to not exceed maximum pipe deflections allowed by ASME B31.9 for building services piping.

Insulated Piping:

Specify parts in first three subparagraphs below as galvanized or painted, as required. Other materials are available in place of wooden blocks.

Attach clamps and spacers to piping.

Piping Operating above Ambient Air Temperature: Clamp may project through insulation.

Piping Operating below Ambient Air Temperature: Use thermal hanger-shield insert with clamp sized to match OD of insert.

Do not exceed pipe stress limits allowed by ASME B31.9 for building services piping.

Install MSS SP-58, Type 39 protection saddles if insulation without vapor barrier is indicated. Fill interior voids with insulation that matches adjoining insulation.

Option: Thermal hanger-shield inserts may be used. Include steel weight-distribution plate for pipe NPS 4 (DN 100) and larger if pipe is installed on rollers.

High-compressive-strength inserts may permit use of shorter shields or shields with less arc span. Revise first subparagraph below to suit Project.

Install MSS SP-58, Type 40 protective shields on cold piping with vapor barrier. Shields shall span an arc of 180 degrees.

Option: Thermal hanger-shield inserts may be used. Include steel weight-distribution plate for pipe NPS 4 (DN 100) and larger if pipe is installed on rollers.

Shield Dimensions for Pipe: Not less than the following:

NPS 1/4 to NPS 3-1/2 (DN 8 to DN 90): 12 inches (305 mm) long and 0.048 inch (1.22 mm) thick.

NPS 4 (DN 100): 12 inches (305 mm) long and 0.06 inch (1.52 mm) thick.

NPS 5 and NPS 6 (DN 125 and DN 150): 18 inches (457 mm) long and 0.06 inch (1.52 mm) thick.

NPS 8 to NPS 14 (DN 200 to DN 350): 24 inches (610 mm) long and 0.075 inch (1.91 mm) thick.

NPS 16 to NPS 24 (DN 400 to DN 600): 24 inches (610 mm) long and 0.105 inch (2.67 mm) thick.

Pipes NPS 8 (DN 200) and Larger: Include wood or reinforced calcium-silicate-insulation inserts of length at least as long as protective shield.

Thermal Hanger Shields: Install with insulation of same thickness as piping insulation.

Isolate piping systems from building structure to minimize noise transfer by using acoustical suspension isolator silencer and bracket system.

Protect tubing and piping from damage caused by abrasion when passing through studs, joists, and similar framing using abrasion protection isolators.

In plenum-rated applications, use tested clamp and isolator support systems designed specifically for this application.

Prevent damage to piping and tubing caused by contact between dissimilar metals using insert system designed specifically for this application.

EQUIPMENT SUPPORTS

Use manufactured equipment supports designed for and recommended by manufacturer for specific applications. Comply with manufacturer's rated load capacities. For applications not suited to, or exceeding, the capacity of manufactured supports, fabricate structural-steel stands to suspend equipment from structure overhead or to support equipment above floor.

Grouting: Place grout under supports for equipment, and make bearing surface smooth.

Provide lateral bracing, to prevent swaying, for equipment supports.

        - No-hub pipe and fitting coupling joints over 4 inches (100 mm) in size shall receive auxiliary support by means of appropriate bracing materials, per U.S. soil pipe and fitting manufacturers' installation instructions, CISPI Designation 301-18 and 310-18, and CISPI Cast Iron Soil Pipe and Fittings Handbook. Auxiliary restraint products used shall be manufactured assemblies with thrust pressure rating adequate for the specific installation and shall be installed onto horizontal joints over 4 inches (100 mm) diameter in size. Field-devised methods and materials shall not be used to accomplish this application solution.

Manufactured pipe hanger and equipment support systems are generally preferable to field-fabricated hangers and supports. If field-fabricated hangers and supports are to be allowed or are otherwise required, retain "Metal Fabrications" Article below and edit to suit Project requirements.

METAL FABRICATIONS

Cut, drill, and fit miscellaneous metal fabrications for [trapeze pipe hangers] [and] [equipment supports].

Fit exposed connections together to form hairline joints. Field weld connections that cannot be shop welded because of shipping size limitations.

Field Welding: Comply with AWS D1.1/D1.1M procedures for shielded, metal arc welding; appearance and quality of welds; and methods used in correcting welding work; and with the following:

Use materials and methods that minimize distortion and develop strength and corrosion resistance of base metals.

Obtain fusion without undercut or overlap.

Remove welding flux immediately.

Finish welds at exposed connections, so no roughness shows after finishing and so contours of welded surfaces match adjacent contours.

ADJUSTING

Hanger Adjustments: Adjust hangers to distribute loads equally on attachments and to achieve indicated slope of pipe.

Trim excess length of continuous-thread hanger and support rods to [1-1/2 inches (40 mm)] <Insert dimension>.

PAINTING

Retain first "Touchup" Paragraph below if Section 099113 "Exterior Painting" or Section 099123 "Interior Painting" is not in Project Manual.

Touchup: Clean field welds and abraded, shop-painted areas. Paint exposed areas immediately after erecting hangers and supports. Use same materials as those used for shop painting. Comply with SSPC-PA 1 requirements for touching up field-painted surfaces.

Apply paint by brush or spray to provide a minimum dry film thickness of 2.0 mils (0.05 mm).

Retain "Touchup" Paragraph below if Section 099113 "Exterior Painting" or Section 099123 "Interior Painting" is in Project Manual. Revise reference if Section 099600 "High-Performance Coatings" applies instead.

Touchup: Cleaning and touchup painting of field welds, bolted connections, and abraded, shop-painted areas on miscellaneous metal are specified in [Section 099113 "Exterior Painting."] [Section 099123 "Interior Painting."] [Section 099600 "High-Performance Coatings."]

Galvanized Surfaces: Clean welds, bolted connections, and abraded areas, and apply galvanizing-repair paint to comply with ASTM A780/A780M.

HANGER AND SUPPORT SCHEDULE

Specific hanger and support requirements are in Sections specifying piping systems and equipment.

Comply with MSS SP-58 for pipe-hanger selections and applications that are not specified in piping system Sections.

Use hangers and supports with galvanized metallic coatings for piping and equipment that will not have field-applied finishes.

Use nonmetallic coatings on attachments for electrolytic protection where attachments are in direct contact with copper tubing.

Use carbon-steel [pipe hangers and supports] [metal trapeze pipe hangers] [and] [metal framing systems] and attachments for general service applications.

Use [stainless steel pipe hangers] [and] [fiberglass pipe hangers] [and] [fiberglass strut systems] and [stainless steel] [or] [corrosion-resistant] attachments for hostile environment applications.

Use copper-plated pipe hangers and [copper] [or] [stainless steel] attachments for copper piping and tubing.

Use padded hangers for piping that is subject to scratching.

Use thermal hanger-shield inserts for insulated piping and tubing.

Horizontal-Piping Hangers and Supports: Unless otherwise indicated and except as specified in piping system Sections, install the following types:

Adjustable, Steel Clevis Hangers (MSS Type 1): For suspension of noninsulated or insulated, stationary pipes NPS 1/2 to NPS 30 (DN 15 to DN 750).

Yoke-Type Pipe Clamps (MSS Type 2): For suspension of up to 1050 deg F (566 deg C) pipes NPS 4 to NPS 24 (DN 100 to DN 600), requiring up to 4 inches (100 mm) of insulation.

Carbon- or Alloy-Steel, Double-Bolt Pipe Clamps (MSS Type 3): For suspension of pipes NPS 3/4 to NPS 36 (DN 20 to DN 900), requiring clamp flexibility and up to 4 inches (100 mm) of insulation.

Steel Pipe Clamps (MSS Type 4): For suspension of cold and hot pipes NPS 1/2 to NPS 24 (DN 15 to DN 600) if little or no insulation is required.

Pipe Hangers (MSS Type 5): For suspension of pipes NPS 1/2 to NPS 4 (DN 15 to DN 100), to allow off-center closure for hanger installation before pipe erection.

Adjustable, Swivel Split- or Solid-Ring Hangers (MSS Type 6): For suspension of noninsulated, stationary pipes NPS 3/4 to NPS 8 (DN 20 to DN 200).

Adjustable, Steel Band Hangers (MSS Type 7): For suspension of noninsulated, stationary pipes NPS 1/2 to NPS 8 (DN 15 to DN 200).

Adjustable Band Hangers (MSS Type 9): For suspension of noninsulated, stationary pipes NPS 1/2 to NPS 8 (DN 15 to DN 200).

Adjustable, Swivel-Ring Band Hangers (MSS Type 10): For suspension of noninsulated, stationary pipes NPS 1/2 to NPS 8 (DN 15 to DN 200).

Split Pipe Ring with or without Turnbuckle Hangers (MSS Type 11): For suspension of noninsulated, stationary pipes NPS 3/8 to NPS 8 (DN 10 to DN 200).

Extension Hinged or Two-Bolt Split Pipe Clamps (MSS Type 12): For suspension of noninsulated, stationary pipes NPS 3/8 to NPS 3 (DN 10 to DN 80).

U-Bolts (MSS Type 24): For support of heavy pipes NPS 1/2 to NPS 30 (DN 15 to DN 750).

Clips (MSS Type 26): For support of insulated pipes not subject to expansion or contraction.

Pipe Saddle Supports (MSS Type 36): For support of pipes NPS 4 to NPS 36 (DN 100 to DN 900), with steel-pipe base stanchion support and cast-iron floor flange or carbon-steel plate.

Pipe Stanchion Saddles (MSS Type 37): For support of pipes NPS 4 to NPS 36 (DN 100 to DN 900), with steel-pipe base stanchion support and cast-iron floor flange or carbon-steel plate, and with U-bolt to retain pipe.

Adjustable Pipe Saddle Supports (MSS Type 38): For stanchion-type support for pipes NPS 2-1/2 to NPS 36 (DN 65 to DN 900) if vertical adjustment is required, with steel-pipe base stanchion support and cast-iron floor flange.

Single-Pipe Rolls (MSS Type 41): For suspension of pipes NPS 1 to NPS 30 (DN 25 to DN 750), from two rods if longitudinal movement caused by expansion and contraction occurs.

Adjustable Roller Hangers (MSS Type 43): For suspension of pipes NPS 2-1/2 to NPS 24 (DN 65 to DN 600), from single rod if horizontal movement caused by expansion and contraction occurs.

Complete Pipe Rolls (MSS Type 44): For support of pipes NPS 2 to NPS 42 (DN 50 to DN 1050) if longitudinal movement caused by expansion and contraction occurs but vertical adjustment is unnecessary.

Pipe Roll and Plate Units (MSS Type 45): For support of pipes NPS 2 to NPS 24 (DN 50 to DN 600) if small horizontal movement caused by expansion and contraction occurs and vertical adjustment is unnecessary.

Adjustable Pipe Roll and Base Units (MSS Type 46): For support of pipes NPS 2 to NPS 30 (DN 50 to DN 750) if vertical and lateral adjustment during installation, in addition to expansion and contraction, is required.

Vertical-Piping Clamps: Unless otherwise indicated and except as specified in piping system Sections, install the following types:

Extension Pipe or Riser Clamps (MSS Type 8): For support of pipe risers NPS 3/4 to NPS 24 (DN 24 to DN 600).

Carbon- or Alloy-Steel Riser Clamps (MSS Type 42): For support of pipe risers NPS 3/4 to NPS 24 (DN 20 to DN 600) if longer ends are required for riser clamps.

Hanger-Rod Attachments: Unless otherwise indicated and except as specified in piping system Sections, install the following types:

Steel Turnbuckles (MSS Type 13): For adjustment of up to 6 inches (150 mm) for heavy loads.

Steel Clevises (MSS Type 14): For 120 to 450 deg F (49 to 232 deg C) piping installations.

Swivel Turnbuckles (MSS Type 15): For use with MSS Type 11 split pipe rings.

Malleable-Iron Sockets (MSS Type 16): For attaching hanger rods to various types of building attachments.

Steel Weldless Eye Nuts (MSS Type 17): For 120 to 450 deg F (49 to 232 deg C) piping installations.

Building Attachments: Unless otherwise indicated and except as specified in piping system Sections, install the following types:

Steel or Malleable-Concrete Inserts (MSS Type 18): For upper attachment to suspend pipe hangers from concrete ceiling.

Top-Beam C-Clamps (MSS Type 19): For use under roof installations with bar-joist construction, to attach to top flange of structural shape.

Side-Beam or Channel Clamps (MSS Type 20): For attaching to bottom flange of beams, channels, or angles.

Center-Beam Clamps (MSS Type 21): For attaching to center of bottom flange of beams.

Welded Beam Attachments (MSS Type 22): For attaching to bottom of beams if loads are considerable and rod sizes are large.

C-Clamps (MSS Type 23): For structural shapes.

Top-Beam Clamps (MSS Type 25): For top of beams if hanger rod is required tangent to flange edge.

Side-Beam Clamps (MSS Type 27): For bottom of steel I-beams.

Steel-Beam Clamps with Eye Nuts (MSS Type 28): For attaching to bottom of steel I-beams for heavy loads.

Linked-Steel Clamps with Eye Nuts (MSS Type 29): For attaching to bottom of steel I-beams for heavy loads, with link extensions.

Malleable-Beam Clamps with Extension Pieces (MSS Type 30): For attaching to structural steel.

Welded-Steel Brackets: For support of pipes from below or for suspending from above by using clip and rod. Use one of the following for indicated loads:

Light (MSS Type 31): 750 lb (340 kg).

Medium (MSS Type 32): 1500 lb (680 kg).

Heavy (MSS Type 33): 3000 lb (1360 kg).

Side-Beam Brackets (MSS Type 34): For sides of steel or wooden beams.

Plate Lugs (MSS Type 57): For attaching to steel beams if flexibility at beam is required.

Horizontal Travelers (MSS Type 58): For supporting piping systems subject to linear horizontal movement where headroom is limited.

Saddles and Shields: Unless otherwise indicated and except as specified in piping system Sections, install the following types:

Steel-Pipe-Covering Protection Saddles (MSS Type 39): To fill interior voids with insulation that matches adjoining insulation.

Protection Shields (MSS Type 40): Of length recommended in writing by manufacturer to prevent crushing insulation.

Thermal Hanger-Shield Inserts: For supporting insulated pipe.

Spring Hangers and Supports: Unless otherwise indicated and except as specified in piping system Sections, install the following types:

Restraint-Control Devices (MSS Type 47): Where indicated to control piping movement.

Spring Cushions (MSS Type 48): For light loads if vertical movement does not exceed 1-1/4 inches (32 mm).

Spring-Cushion Roll Hangers (MSS Type 49): For equipping Type 41 roll hanger with springs.

Spring Sway Braces (MSS Type 50): To retard sway, shock, vibration, or thermal expansion in piping systems.

Variable-Spring Hangers (MSS Type 51): Preset to indicated load, and limit variability factor to 25 percent to allow expansion and contraction of piping system from hanger.

Variable-Spring Base Supports (MSS Type 52): Preset to indicated load, and limit variability factor to 25 percent to allow expansion and contraction of piping system from base support.

Variable-Spring Trapeze Hangers (MSS Type 53): Preset to indicated load, and limit variability factor to 25 percent to allow expansion and contraction of piping system from trapeze support.

Constant Supports: For critical piping stress and if necessary to avoid transfer of stress from one support to another support, critical terminal, or connected equipment. Include auxiliary stops for erection, hydrostatic test, and load-adjustment capability. These supports include the following types:

Horizontal (MSS Type 54): Mounted horizontally.

Vertical (MSS Type 55): Mounted vertically.

Trapeze (MSS Type 56): Two vertical-type supports and one trapeze member.

Comply with MSS SP-58 for trapeze pipe-hanger selections and applications that are not specified in piping system Sections.

Comply with MFMA-103 for metal framing system selections and applications that are not specified in piping system Sections.

Verify suitability of fasteners in this article for use in lightweight concrete or concrete slabs less than 4 inches (100 mm) thick. Powder-actuated fasteners may be banned for use in certain occupancies. Consult authorities having jurisdiction and the Owner's project requirements.

Use [powder-actuated fasteners] [or] [mechanical-expansion anchors] instead of building attachments where required in concrete construction.

Use pipe-positioning systems in pipe spaces behind plumbing fixtures to support supply and waste piping for plumbing fixtures.

END OF SECTION 220529